## Sheet1
Subaddress: 0x01; 8 bits, 1 start, 1 stop, no parity, baud rate 9600
Modbus: command 0x03 (read multiple parameters, up to 8 parameters at a time), 0x06 (write a single parameter), the data is a 16bit signed integer, and the displayed value is the product of the signed integer and the data precision;
Serial number and mailing address | name | scope/significance | default | Data Accuracy |  | state | Remark
P00（0） | On-off | 1 - Power on 0 - Power off | 0 | 1
P01（1） | Mode | 0 AC cooling | 1 | 1
1 AC heating
2 DHW
3 Cooling+DHW
4 Heating+DHW
P02（2） | Heating target temperature | 10~55℃(AU) | 45℃ | 1
P03（3） | Cooling target temperature | 10~25℃ | 12℃ | 1
P04（4） | Domestic hot water target temperature | 10~60℃(AU) | 50℃ | 1
P05（5） | Indoor target temperature | 18~35℃ | 21℃ | 1
P06（6） | AC water temperature difference | 1~15℃ | 2℃ | 0.5
P07（7） | DHW water temperature difference | 2~15℃ | 3℃ | 0.5
P08（8） | Domestic hot water AU option | 0-Disabled 1-enable | 1 | 1
P09（9） | Hot water max frequency | 2~10 | 10 | 1
P10（10） | Sterilization interval days | 1~99 days | 7 | 1
P11（11） | Sterilization start time | 0~23:00 | 1 | 1
P12（12） | Sterilization running time | 5~99mins | 10 | 1
P13（13） | Sterilization temperature | 50~75℃ | 70 | 1
P14（14） | Force sterilization | 0-No execution 1-Execution 2-Sterilization function is invalid | 0 | 1
P15（15） | Domestic hot water function selection | 0-invalid 1-valid | 1 | 1
P16（16） | Hot water circulation pump working mode | 1 timing 2 temperature difference 3 timing + temperature difference | 3 | 1 | When P17=0 and the switching time is 0:00, P16=0 (water pump is invalid)
P17（17） | Hot water circulating pump starting temperature difference | 0~20℃ | 5℃ | 1
P18（18） | Heating AU maximum temperature | 35~50℃ | 45℃ | 1
P19（19） | Heating AU offset temperature | -15~15℃ | 0℃ | 1
P20（20） | Air conditioner heating AU switch | 0-Disabled 1-enable | 1 | 1
P21（21） | Night run mode starting time | 0~23h | 22 | 1
P22（22） | Night run mode stop time | 0~23h | 6 | 1
P23（23） | Night run mode active option | 0-Disabled 1-enable | 0 | 1
P24（24） | Water pump working mode | 0(Non-stop)、1（Stop at temperature）、 | 0 | 1
2 (stop for 15 minutes, open for 1 minute)
P25（25） | Water pump antifreeze time | 5~50mins | 30 | 1
P26（26） | Water pump speed regulation temperature difference | 3~8℃ | 5℃ | 1
P27（27） | PWM water pump minimum speed | 2~8,correspond20~80%speed | 6 | 1
P28（28） | Ambient temperature of electric auxiliary heat start of air conditioner | -30~20℃ | 0 | 1
P29（29） | Hot water and electric auxiliary heat start ambient temperature | -30~20℃ | 0 | 1
P30（30） | Electric heating stop offset temperature | 1~15℃ | 2 | 1
P31（31） | E2 connection port function definition | 0: electric heating; 1: second heat source | 0 | 1
P32（32） | Second heat source starting temperature | -30~20℃ | -15℃ | 1
P33（33） | Air conditioner antifreeze temperature | -15~5℃ | 3 | 1
P34（34） | defrosting method | 0: Mode 1; 1: Mode 2; 2: Manual | 0 | 1
P35（35） | Defrost start temperature | -8~2℃ | -2 | 1
P36（36） | Defrost Interval Multiplier | 0: no defrosting; 1; 2; 3; 4: (interval X4) | 1 | 1
P37（37） | First defrost interval | 15~99mins | 35 | 1
P38（38） | Compressor defrost frequency | 30~90Hz | 60HZ | 1
P39（39） | Defrost exit temperature | 5~30℃ | 20 | 1
P40（40） | Maximum defrost time | 2~20min | 15 | 1
P41（41） | defrost mode 2 temp difference | 0~10°C | 3°C | 1
P42（42） | defrost mode 2 pressure difference | 0.01~1.0MPa | 0.1 | 0.01
P43（43） | EC fan maximum speed | 500~1500RPM | 900RPM | 1
P44（44） | Heating fan speed regulation temperature difference | 2~15℃ | 6 | 1
P45（45） | Cooling fan speed regulation temperature difference | 3~18℃ | 8 | 1
P46（46） | EC fan speed control | 0: manual, 1: automatic | 1 | 1
P47（47） | EC fan manual speed | 0~1500RPM | 0 | 1
P48（48） | Inverter compressor model setting | 0~999， | 1 | 1
P49（49） | Operating the set frequency function | 0: manual, 1: automatic | 1 | 1
P50（50） | Debug fixed operating frequency | 10~100 Hz | 50HZ | 1
P51（51） | Compressor frequency limiting current | 1~50A | 14.5A | 0.1
P52（52） | Compressor down frequency current | 1~50A | 15.5A | 0.1
P53（53） | Compressor shutdown current | 1~50A | 17A | 0.1
P54（54） | Compressor maximum frequency | 50~120Hz | 60HZ | 1
P55（55） | Compressor minimum frequency | 20~50Hz | 30HZ | 1
P56（56） | Air conditioner water flow switch type selection | 0: water flow switch; 1: flow meter | 0 | 1
P57（57） | Air conditioner minimum water flow | 3~80L/min, step 1 | 20 | 1
P58（58） | Air conditioning function selection | 0: hot and cold 1: cold only 2: hot only | 0 | 1
P59（59） | Water source air cooling option | 0-air cooling, 1-water source | 0 | 1
P60（60） | Power-down recovery function bit | 0-no, 1-yes | 1 | 1
P61（61） | Main valve control mode | 0: None 1: Look-up table 2: Manual 3: Automatic | 3 | 1
P62（62） | Main valve initial opening (manual opening adjustment) heating | 50~480 | 400 | 1
P63（63） | Main valve initial opening (manual opening adjustment) cooling | 50~480 | 400 | 1
P64（64） | Main valve superheat (heating) | -5~10℃ | 0 | 1
P65（65） | Main valve superheat (cooling) | -5~10℃ | 0 | 1
P66（66） | Enthalpy injection valve control mode | 0: None 1: Look-up table 2: Manual 3: Automatic | 3 | 1
P67（67） | Initial opening of enthalpy injection valve (manual opening adjustment) for heating | 40~480 | 40 | 1
P68（68） | Enthalpy injection valve opening exhaust temperature (heating) | 50~120℃ | 70 | 1
P69（69） | Enthalpy injection valve opening exhaust temperature (cooling) | 50~120℃ | 75 | 1
P70（70） | Enthalpy injection valve closing valve exhaust temperature hysteresis | 2~20℃ | 10 | 1
P71（71） | Enthalpy injection valve closed valve ambient temperature hysteresis | 2~10℃ | 5 | 1
P72（72） | Enthalpy injection valve opening ambient temperature (heating) | -15~20℃ | 7 | 1
P73（73） | Enthalpy injection valve opening ambient temperature (cooling) | 20~80℃ | 35 | 1
P74（74） | Pressure sensor enable bit | 0-pressure sensor, 1-pressure switch | 1 | 1
P75（75） | Air conditioning mode frequency limit pressure | 2.0~4.5MPa | 3.9MPa | 0.1 |  |  | Remark
P76（76） | Air-conditioning mode cancels frequency limit pressure | 2.0~4.5MPa | 3.6MPa | 0.1 |  |  | Remark
P77（77） | Hot water mode frequency limiting pressure | 2.0~4.5MPa | 3.9MPa | 0.1 |  |  | Remark
P78（78） | Hot water mode cancels frequency limit pressure | 2.0~4.5MPa | 3.6MPa | 0.1 |  |  | Remark
P79（79） | High pressure protection setting value | 2.5~5.0MPa | 4.3MPa | 0.1 |  |  | Remark
P80（80） | Low pressuree protection set point | 0.01~1.0MPa | 0.1MPa | 0.01 |  |  | Remark
P81（81） | High pressure protection release hysteresis | 0.2~1.5MPa | 0.5MPa | 0.01
P82（82） | Low pressure protection release hysteresis | 0.01~1.0MPa | 0.15MPa | 0.01
P83（83） | Electric heating control mode | 0: manual, 1: automatic | 1 | 1
-84
P84（85） | Reporting frequency | 30~9999s | 300 | 1 |  |  | Remark
P85（86） | Reset | 0: no recovery 1: recovery | 0 | 1 |  |  | The wire controller reports data to the background
P86（87） | User password setting |  | 9999 | 1
P87（88） | Administrator password setting |  | 9999 | 1
P88（89） | Chassis heating start ambient temperature | -25~2℃ | 0 ºC | 1
P89（90） | hot water coil | 0: no, 1: yes | 1 | 1
F000~ | The minimum value of the adjustment range of the above parameters | The data is a 16bit signed integer
F200~ | The maximum value of the adjustment range of the above parameters | The data is a 16bit signed integer
100 | RTC hour, minute | High byte hour 0~23, low byte minute 0~59
101 | Timing status of hot water circulating pump | 0: Out of the scheduled time period; 1: Scheduled open time period
102 | Hot water circulation pump timing mode | 0 invalid, 1 timing, 2 temperature difference, 3 timing + temperature difference
103 | Hot water circulation pump timing temperature difference | 0~20℃
Communicate with the wire controller to query the status query table
Serial number and mailing address | Name | Range/Meaning | default | Data Accuracy |  | state | Remark
C00（200） | External coil temperature | -30~97℃ | None | 0.5℃ |  | Inquire
C01（201） | Exhaust gas temperature | -30~128℃ | None | 0.5℃ |  | Inquire
C02（202） | Ambient temperature | -30~97℃ | None | 0.5℃ |  | Inquire
C03（203） | Return gas temperature | -30~97℃ | None | 0.5℃ |  | Inquire
C04（204） | EVI inlet temperature | -30~97℃ | None | 0.5℃ |  | Inquire
C05（205） | EVI outlet temperature | -30~97℃ | None | 0.5℃ |  | Inquire
C06（206） | Internal coil temperature | -30~97℃ | None | 0.5℃ |  | Inquire
C07（207） | Inlet temperature | -30~97℃ | None | 0.5℃ |  | Inquire
C08（208） | water temperature | -30~97℃ | None | 0.5℃ |  | Inquire
C09（209） | domestic hot water temperature | -30~97℃ | None | 0.5℃ |  | Inquire
C10（210） | hot water pipe temperature | -30~97℃ | None | 0.5℃ |  | Inquire
C11（211） | Room temperature | -30~97℃ | None | 0.5℃ |  | Inquire
C12（212） | Solar temperature | -30~97℃ | None | 0.5℃ |  | Inquire
C13（213） | Outer water flow rate | 0~120L/min | None | 1 |  | Inquire
C14（214） | Inner water flow rate | 0~120L/min | None | 1 |  | Inquire
C15（215） | ctual overheat degree of main expansion valve | -30~97℃ | None | 0.5℃ |  | Inquire
C16（216） | Actual overheat degree of injection enthalpy valve | -30~97℃ | None | 0.5℃ |  | Inquire
C17（217） | high pressure | 0-5.0MPa | None | 0.1 |  | Inquire
C18（218） | low pressure | 0-2.0MPa | None | 0.1 |  | Inquire
C19（219） | High pressure switch status | 1(connected);0(disconnect) | None | 1 |  | Inquire
C20（220） | Low pressure switch status | 1(connected);0(disconnect) | None | 1 |  | Inquire
C21（221） | Temperature control switch status | 1(connected);0(disconnect) | None | 1 |  | Inquire
C22（222） | Internal water flow switch status | 1(connected);0(disconnect) | None | 1 |  | Inquire
C23（223） | Outer water flow switch status | 1(connected);0(disconnect) | None | 1 |  | Inquire
C24（224） | Cooling switch status | 1(connected);0(disconnect) | None | 1 |  | Inquire
C25（225） | Heating switch status | 1(connected);0(disconnect) | None | 1 |  | Inquire
C26（226） | Phase sequence state | 1(normal);0(wrong phase or lack of phase) | None | 1 |  | Inquire
C27（227） | defrost state | 1(defrosting);0(no defrost symbol) | None | 1 |  | Inquire
C28（228） | Sterilize state | 1(sterilizing);0(not sterilizing) | None | 1 |  | Inquire
C29（229） | Antifreeze state | 1(antifreezing);0(not antifreezing) | None | 1 |  | Inquire
C30（230） | compressor | Display mechanical operating frequency | None | 1 |  | Inquire
C31（231） | outdoor fan1 | display speed | None | 1 |  | Inquire
C32（232） | outdoor fan2 | display speed | None | 1 |  | Inquire
C33（233） | water pump1 state | 1:run;0:stop | None | 1 |  | Inquire
C34（234） | water pump2 state | 1:run;0:stop | None | 1 |  | Inquire
C35（235） | water pump3 state | 1:run;0:stop | None | 1 |  | Inquire
C36（236） | water pump4 state | 1:run;0:stop | None | 1 |  | Inquire
C37（237） | water pump5 state | 1:run;0:stop | None | 1 |  | Inquire
C38（238） | bypass valve | 1:run;0:stop | None | 1 |  | Inquire
C39（239） | EVI electromagnetic valve | 1:run;0:stop | None | 1 |  | Inquire
C40（240） | Four-way valve status | 1:run;0:stop | None | 1 |  | Inquire
C41（241） | Air conditioner electric heating status | 1:run;0:stop | None | 1 |  | Inquire
C42（242） | Domestic hot water electric heating status | 1:run;0:stop | None | 1 |  | Inquire
C43（243） | Crankshaft heater status | 1:run;0:stop | None | 1 |  | Inquire
C44（244） | Three-way valve 1 state | 1:run;0:stop | None | 1 |  | Inquire
C45（245） | Three-way valve 2 state | 1:run;0:stop | None | 1 |  | Inquire
C46（246） | Three-way valve 3 state | 1:run;0:stop | None | 1 |  | Inquire
C47（247） | Main expansion valve opening | 0-500 | None | 1 |  | Inquire
C48（248） | Enthalpy injection expansion valve opening | 0-500 | None | 1 |  | Inquire
C49（249） | Compressor start and stop times | 0-1000 | None | 1 |  | Inquire
C50（250） | Compressor running time | 0-1000h | None | 1 |  | Inquire
C51（251） | Current working mode | 0-AC cooling, 1-AC heating, 2-DHW | None | 1 |  | Inquire
C52（252） | Total defrosting times |  | None | 1 |  | Inquire
C53（253） | Compressor target frequency |  | None | 1 |  | Inquire
C54（254） | Compressor input current |  | None | 0.1A |  | Inquire
C55（255） | Outdoor unit module temp. |  | None | 0.5℃ |  | Inquire
C56（256） | Inverter running code1 |  | None | 1 |  | Inquire
C57（257） | Inverter running code2 |  | None | 1 |  | Inquire
C58（258） | Inverter running code3 |  | None | 1 |  | Inquire
C59（259） | Compressor Error Codes |  | None | 1 |  | Inquire
C60（260） | IPM fan | IPM fan 1:run;0:stop | None | 1 |  | Inquire | Not mentioned
C61（261） | Tc |  |  | 1
C62（262） | Ts |  |  | 1
C63（263） | P |  |  | 1
C64（264） | Main board program version | 0-9999 | None | 1 |  | Inquire
C65（265） | Driver module program version | 0-9999 | None | 1 |  | Inquire
C66（266） | Chassis Electric Heating Status | 1:run;0:stop | None | 1 |  | Inquire
When the machine is faulty, it will display "Ex", communication address: 140~145, start to discharge from bit0 of 140
No. | fault meaning |  |  | code | Remark
1 | Outdoor air temp sensor error |  |  | E1 | Outdoor air temp sensor open circuit or short circuit
2 | Coil temp sensor error |  |  | E2 | Coil temperature sensor open circuit or short circuit
3 | Suction temp sensor error |  |  | E3 | Suction temp sensor open circuit or short circuit
4 | Discharge temp sensor error |  |  | E4 | Discharge temp sensor open circuit or short circuit
5 | Liquid refrigerant temp sensor error |  |  | E5 | Sensor open circuit or short circuit
6 | EVI inlet temp sensor error |  |  | E6 | EVI inlet temp sensor open circuit or short circuit
7 | EVI outlet temp sensor error |  |  | E7 | EVI outlet temp sensor open circuit or short circuit
8 | DHW temp sensor error |  |  | E8 | DHW temp sensor open circuit or short circuit
9 | A/C outlet temp sensor error |  |  | E9 | A/C outlet temp sensor open circuit or short circuit
10 | A/C inlet temp sensor error |  |  | E10 | A/C inlet temp sensor open circuit or short circuit
11 | Indoor air temp sensor error |  |  | E11 | Indoor air temp sensor open circuit or short circuit
12 | Solar temp sensor error |  |  | E12 | Solar temp sensor open circuit or short circuit
13 | DHW pipe temp sensor error |  |  | E13 | DHW pipe temp sensor open circuit or short circuit
14 | High pressure sensor error |  |  | E14 | 1.sensor fault 2.open circuit or short circuit 3. PCB fault
15 | Low pressure sensor error |  |  | E15 | 1.sensor fault 2.open circuit or short circuit 3. PCB fault
16 | High pressure protection |  |  | E16 | 1.refrigerant volume too much 2.throtting part error,
3. High pressure switch error
17 | Low pressure protection |  |  | E17 | 1.refrigerant volume too little 2.throtting part error,
18 | Inside Water flow error |  |  | E18 | 1.Water flow volume too small 2. Water flow switch error
19 | Outside Water flow error |  |  | E19 | 1.Water flow volume too small 2. Water flow switch error
20 | Communication error |  |  | E20 | Communication wire open or PCB or Wired controller fault
21 | Communication error(IPM and PCB) |  |  | E21 | Communication wire open or PCB or IPM fault
22 | Discharge high temp protection |  |  | E22 | 1.refrigerant volume too little。2.throtting part error
23 | Coil high temp protection |  |  | E23 | 1. refrigerant volume too much, 2.throtting part error,
24 | Over current protection(PCB) |  |  | E24 | AC current value over the setting value
25 | IPM high temp protection |  |  | E25 | IPM module temp higher than setting value（radiator）
26 | Power voltage protection(PCB) |  |  | E26 | Voltage is too high or too low, heat pump will recover when voltage be normal (165~265VAC)
27 | Over current protection (IPM) |  |  | E27 | IPM current over（bus current）
28 | IPM error |  |  | E28 | IPM fault
29 | System anti-freeze twice |  |  | E29 | The antifreeze function in A/C mode has been
30 | Temp differential too big |  |  | E30
31 | DHW anti-freeze twice |  |  | E31 | The antifreeze function in DHW mode has been
32 | pressure protection twice |  |  | E32 | High or low pressure protection twice in 30minutes
33 | Compressor fail to start up |  |  | E33 | Compressor cannot start properly or software error（Rotating speed）
34 | Compressor over current (IPM) |  |  | E34 | Compressor current too high（line current）
35 | Miss phase |  |  | E35 | Power supply error（input side）
36 | IPM current sensor error |  |  | E36 | Sensor fault
37 | IPM high temp protection |  |  | E37 | IPM temperature too high（Bring its own）
38 | PFC error |  |  | E38 | PFC fault
39 | DC voltage too high |  |  | E39 | DC voltage higher than 395V
40 | DC voltage too low |  |  | E40 | DC voltage lower than 300V
41 | Power voltage protection(IPM) |  |  | E41 | IPM Voltage is too high or too low
42 | Over current protection (IPM) |  |  | E42 | IPM current is too high
43 | Power voltage test error |  |  | E43 | IPM fault
44 | DSP and PFC communication error |  |  | E44 | IPM fault
45 | IPM temp sensor error |  |  | E45 | IPM temp sensor fault
46 | DSP communication error |  |  | E46 | IPM fault
47 | IPM module high temp protection |  |  | E47 | Module temperature is too high
48 | 1# EC motor error |  |  | E48 | Motor fault
49 | 2# EC motor error |  |  | E49 | Motor fault
50 | Voltage protection(15V) |  |  | E50 | Voltage is too high or too low
51 | Model does not match |  |  | E51 | Model does not match